PennBarry Fan Guide Specification

Mixed Flow (tubular Inline fan): Model MXI for belt drive and direct drive
This documents copyrights 2017 PennBarry
Mixed flow Inline fans is a tubular mixed flow fan utilizing highly efficient mixed flow wheel suitable for supply, exhaust, or return air applications. 

Description

Mixed flow tubular Inline fan is compact and lightweight design which combines the high volume advantage of axial fans with low sound and higher efficiency of centrifugal fans, and, through its versatility it even surpasses the efficiency of traditional axial and centrifugal fan technology. Moreover, the outstanding air and sound performance of this fan sets it apart from the competition. 

Product Capabilities

· Model: MXI Belt Drive and Direct drive
• Size range from 122 – 600

• Static pressure up to 8 in. wg.

• Flow capacity up to 113,600 CFM

Note to Specifier: This product specification guide is written in accordance to the Construction Specifications Institute (CSI) Master Format - 2016 Edition.

[REMOVED DESCRIPTION AND MODEL CAPABILITIES TO AVOID REPEATATION OF INFORMATION] 
Note to Specifier: This product specification guide is written in accordance to the Construction Specifications Institute (CSI) Master Format - 2016 Edition.

BEGIN SECTION 23 34 23
1. GENERAL
1.1 SUMMARY
A. Section covers Single and twin unit centrifugal cabinet fan, Zephyr (Z & ZCC), belt drive.
1.2 REFERENCE STANDARDS AND CERITIFICATIONS
A. Air Movement and Control Association Inc. (AMCA):

1. 99 - Standards Handbook

2. 200 - Publication, Air Systems

3. 201-90 - Publication, Fans and Systems

4. 202-88 - Publication, Troubleshooting

5. 203-90 - Publication, Field Performance Measurement of Fan Systems

6. 211-05 - Publication, Certified Ratings Program – Product Rating Manual for Fan Air Performance

7. 300-96 - Standard Reverberant Room Method for Sound Testing of Fans

8. 311-05 - Publication Certified Ratings Program – Product Rating Manual for Fan Sound Performance

9. 99-0401-86 - Classification for Spark Resistant Construction

10. 99-2408-69 - Operating Limits for Centrifugal Fans

B. Air Movement and Control Association Inc. (AMCA), American National Standards Institute (ANSI):

1. 204-05 - Standard Balance Quality and Vibration Levels for Fans

2. 210-99 - Standard Laboratory Methods of Testing Fans for Aerodynamic Performance Rating

C. American National Standards Institute (ANSI):

1. 11-r1999 - Method of Evaluating Load Ratings of Bearings 

D. American Society of Civil Engineers (ASCE):

1. 7-02 - Minimum Design Loads for Building and Other Structures

E. American Society of Heating, Refrigerating and Air Conditioning Engineers, Inc. (ASHRAE):

1. Chapter 45 - 2003 Handbook, HVAC Applications

2. Chapter 7 - 2001 Fundamentals handbook, Sound-Vibration

3. Chapter 32 - 2001 Fundamentals handbook, Duct Design

4. Chapter 18 - 1992 HVAC System and Equipment handbook, Fans

F. American Society for Testing and Materials (ASTM):

1. E330-02 - Standard Test Method for Structural Performance of Exterior Windows, Doors, Skylight and Curtain Walls by Uniform Static Air Pressure Difference

G. National Fire Protection Association (NFPA)

1. 70 - National Electrical Code

2. 90A-02 - Standard for the Installation of Air-Conditioning and Ventilating Systems

3. 92A-06 - Recommend Practice for Smoke-Control System

4. 92B-05 - Standard for Smoke Management System in Malls, Atria, and Large Areas

5. 96-04 - Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations
H. Occupational Safety and Health Administration (OSHA):

1. 1910.212 - General requirements for Machine Guarding

2. 1910.219 - General requirements for guarding safe use of mechanical power transmission apparatus

3. 1926.300 - General requirements for safe operation and maintenance of hand and power tools

I. Underwriters Laboratories (UL):

1. 705 - Standard Power Ventilators

2. Power Ventilators for Smoke Control Systems

3. 762 - Standard Power Roof Ventilators for Restaurant Exhaust Appliances

1.3 SUBMITTALS

A. Submit in accordance with CSI Master Format 01 33 00 Submittal Procedures

B. Fan Performance

1. Provide air performance curves with the flow, static pressure and horsepower

2. Provide sound performance data with sound power levels in eight octave bands, A-weighted overall sound power, and sones level

3. Provide motor electrical characteristics including current, voltage, phase, cycle, enclosure, nominal speed
4. List all accessories equipped with fan

5. List Standard features of fan

6. Provide dimensional drawings including weight

7. Provide documentation of AMCA and UL certification

1.4 QUALITY ASSURANCE

A. Fan Performance Certification

1. Fans rating must conform to tests and procedures performed in accordance with AMCA Publication 211 & 311 and comply with the requirements of the AMCA Certified Ratings Program

2. Fans must bear AMCA licensed Ratings Seal for Air & Sound Performance.

3. Fan shall be UL 705, 762 and 793 certified.

B. Electrical

1. Motors must comply with NEMA standards

1.5 LOGISTICS AND STARTUPS
A. Delivery

1. Units must be examined for damage before leaving the factory.
2. Unit shall be inspect for any signs of tampering to carton or unit damage during transit and check for loose, missing or damaged parts. If units are damaged in transit, it is the responsibility of the receiver to make all claims against the carrier.

B. Handling

1. Fans should be handled in accordance with manufacturer’s instructions and follow all relevant safety precautions in accordance with OSHA regulations 
2. Mishandling of units and incorrect lifting causing damage to the fan will void the warranty.

C. Storage

1. Product must be stored on a level, solid surface, preferably indoors. If outside storage is necessary, protect the units against moisture and dirt by encasing the cartons in plastic or in some similar weatherproof material.

2. Long term storage requires special attention and should follow instructions noted in the product’s Operation and Maintenance Manual.

1.6 WARRANTY
A. Manufacturer’s warranty

1. Warranty period is 12 months from date of shipment.

2. See Manufacturer’s warranty for specific terms & conditions.
2. PRODUCTS
1.7  MANUFACTURER
A. PennBarry, Lebanon, Indiana 46052. 

1.8 MIXED FLOW TUBULAR INLINE FAN, BELT DRIVE AND DIRECT DRIVE.

A. Basis of Design: PennBarry Model: MXI
B. General Description:
1. Unit(s) shall have tubular inline fan, suitable for supply, exhaust, or return air applications.
2. Unit(s) shall consist of highly efficient mixed flow wheel including straightening vanes.
3. Unit(s) shall be compact and light weight design which combines the high volume advantage of axial fans with low sound and higher efficiency of centrifugal fans
4. Unit(s) shall have below performance capabilities,
· Static pressure up to 8.3” wg. 

· Flow capacity up to 113,600 CFM. 
5. Unit(s) shall be available in sizes ranging from 122 thru 600.
6. Each fan shall be belt drive in AMCA arrangement 9 and direct drive in AMCA arrangement 4.
7. Unit(s) shall be able to propel air temperatures up to 180 deg. F in its standard construction.

8. Each fan shall bear the AMCA Licensed Ratings seal for Air and Sound Performance, and shall be UL and cUL listed
9. Unit(s) shall be statically and dynamically balanced.
10. Unit(s) shall be available in Construction Levels 1 and 2.
C. Construction:
1. Unit(s) housing shall be continuously welded and constructed of heavy gauge steel.
2. Unit(s) shall incorporate flexible mounting either ceiling hung or base mounted, making it suitable for both horizontal and vertical applications

3. Unit(s) shall have the provision of eight mounting brackets and 4 bolt on feet for enabling flexible mounting.
4. Unit(s) shall be available in either of the spark resistant construction, AMCA “C” construction or AMCA “B” construction.
5. Unit(s) with belt drive shall be available in following configuration as per the application / requirement,

a) Grease Exhaust configuration

· Unit(s) with Grease Exhaust configuration shall be UL 762 listed 

· Unit(s) shall meet the requirements according to NFPA 96.
· Unit(s) shall include pre-wired weather resistant junction box and grease collector box.

· [Optional] Unit(s) consisting of upblast mounting shall be attached to fully welded inlet plenum and mounted on a curb cap

· Unit(s) shall consist of integral galvanized curb caps.

· Unit(s) shall be provided with high temperature sealant between scroll casing and sides

· Unit(s) shall be designed for high velocity discharge.

b) Heat and smoke configuration

· Unit(s) with heat and smoke configuration shall be listed as per UL 705, UL793, Industrial Risk Insurers (IRI) and Southern Building Code Congress International (SBCCI).

· Unit(s) shall be equipped with steel wheel and extended lube lines.

· Unit(s) shall be compatible with temperature of 500 deg. F for 4 hours and 1000 deg. F. for 41 minutes.
D. Wheel:
1. Wheel(s) shall consist of a mixed flow, centrifugal, highly efficient, steel (and aluminum option), and non-overloading. Wheel(s) shall be dynamically balanced to AMCA 204-5/ANSI S2.19 – Balance Quality Grade G 6.3.
2. Wheel(s) shall consist of a contoured flat and die formed airfoil blade design.  Blades shall be continuously welded to the wheel shroud and wheel hub cone.
3. Wheel(s) hubs shall be keyed and securely attached the fan, or motor shaft.

E. Motors:
1. Motor Type: AC Induction Motor [ Belt Drive, Arrangement 9 only]

a) Motor enclosure shall be available in various options such as ODP, TEFC, SGR and EXP.

b) Motors shall be provided with permanently lubricated, continuous duty ball bearing design furnished at the specified voltage, phase, and enclosure.

c) Labelled with electrical specifications.

d) Drive belts and sheaves shall be sized for 1.5 service factor of the fan operating brake horsepower, and shall be readily and easily accessible for service, if required.

e) Motors shall be capacitor start – capacitor run type, starter not required.
F. Speed Controller : [Direct Drive, Arrangement 4 only]

1. Unit(s) shall be provided with speed controller for adjusting the motor rpm.
2. Unit(s) Speed controller shall be IP 22 or IP 52 rated.
3. This provision shall be available with direct drive, arrangement 4 only.

G. Shafts and Bearings : [Belt drive, Arrangement 9 only]
1. Unit(s) shall utilize durable and long life ball bearing having minimum L10 life rating of 80,000 hours.

2. [Optional] Unit(s) shall be provided with extended life bearing with an L10 life of 200,000 hours.
3. Unit(s) shafts shall ride on ball bearings for quiet operation with the concentric lock mechanism.
4. Unit(s) shall consist of precisely turned, ground and polished solid steel shafts..
H. Extended lube lines :

1. Unit(s) shall incorporate factory installed polyamide or copper extended lube lines.
I. Slip fit inlet and outlet :

1. Unit(s) shall be equipped with a slip fit inlet and outlet as standard.
J. Belt Guard : [Arrangement 9, only] 
1. Unit(s) shall be equipped totally enclosed belt guards meeting OSHA standards.

K. Options/Accessories:
1. Access Door:
a) Unit(s) shall be provided with bolted or hinged access door.
2. Weather Covers:

a) Unit(s) shall be equipped with weather cover providing protective covering.

b) Unit(s) weather cover shall enclose the drive assembly, motor, shaft and bearing.

3. Belt tunnel:

a) Unit(s) shall be equipped with belt tunnel in order to prevent damage to fan belts.

b) Unit(s) belt tunnel shall be constructed of steel.
4. Shaft Seal:

a) Unit(s) shall be equipped with a heat resistant ceramic fiber material.

b) [Optional] Unit(s) shall be supplied with Neoprene seals, if required.
5. Mounting Channel Assembly:

a) Unit(s) shall be provided with mounting channel assembly in ceiling arrangement.

6. Safety Service Switch

a) Safety switches shall be provided to allow positive electrical shut-off and safety.
b) Units shall be prewired to a junction box mounted in the motor compartment and equipped with an electrical disconnect device (except explosion proof).

c) Unit(s) shall be provided with a wide range of NEMA rated enclosures with safety switches available for,

i. NEMA 1 (Indoor) 

ii. NEMA 3R (Weather proof)

iii. NEMA 4 (outdoor)
d) Safety switch NEMA 1 and 3R switch shall be factory wired and remaining shall be shipped loose.

e) Safety service switches shall be field wired by a licensed electrician.
7. Inlet and outlet guards : 
a) Unit(s) shall be provided with inlet and outlet guards.
b) Unit(s) inlet guards shall be heavy gauge zinc plated steel wire.

c) Unit(s) outlet guards shall be heavy gauge wire.
8. Drains : 

a) Unit(s) shall be available with provision of drains at the lowest point of scroll.

b) Unit(s) drains shall be standard type ¾” NPT external thread with plug.
9. Paints / Coating:

a) Unit shall be powder coated. Coatings such as standard enamel, airdry phenolic with UV protection or Special coat shall be available.
10. Vibration Isolation:

a) Unit(s) shall be supplied with rubber-in-shear and spring type vibration hangers.
b) Vibration isolators shall be sized to match the weight of each fan
11. Flexible duct connectors : 

a) Unit(s) shall be provided with duct connectors for both indoor and outdoor installations.
12. Flanges : 

a) Unit(s) shall be provided with flanges where the fan is required to be connected to the duct work.
b) If necessary, companion flanges shall be provided. 
13. Variable Frequency Drive (VFD): 
a) Unit shall be provided with variable frequency drive (VFD) to meet performance requirement while increasing the efficiency.

b) VFD shall be ideal for both new and retrofit applications.

c) Variable frequency drive shall be available in both loose and factory mounted configuration. 

3. EXECUTION
1.9 MANUFACTURER’S INSTRUCTION
A. Follow all manufacturers product usage guidelines and installation instructions

1.10 EXAMINATION
A. Examine fans upon delivery for visual check of components.  Verify no visible external damage.  Examine area of fan installation for non-satisfactory conditions that may cause increased maintenance or increased difficulty of installation. Notify Engineer of these conditions and correct as is necessary. 

1.11 PREPARATION
A. Verify Roof openings are square and fan dimensions match.  Verify fan motor electrical matches building supply power.
1.12 INSTALLATION
A. Follow manufacturer’s recommendations as dictated in the Installation, Operations, & Maintenance Manual

1.13 SYSTEM STARTUP
A. Follow manufacturer’s recommendations as dictated in the Installation, Operations, & Maintenance Manual

1.14 MAINTENANCE 

A. Follow manufacturer’s recommended schedule as specified in the Installation, Operations, & Maintenance Manual

B. Failure to comply with proper maintenance will void Manufacturer’s Warranty

END OF SECTION 23 34 23
