
PennBarry Fan Guide Specification Tubular Centrifugal Inline Fan: Model TCI

This document copyrights© 2022 PennBarry
TCI is a light industrial airfoil tubular centrifugal inline fan that delivers reliable air performance. TCI can be either ceiling hung or floor mounted, making it suitable for both horizontal and vertical applications. 
Utilizing an all-aluminum airfoil non-overloading impeller, TCI provides a higher level of efficiency. Every part of the fan airstream is designed and manufactured to produce the highest results under rated operating conditions.
The TCI features AMCA type “B” Spark resistant construction and offers industry leading air performance compared to similar products in the market. The centrifugal wheels are aluminum, non-overloading, Airfoil, robotically welded, and dynamically balanced.
Product Capabilities
-
Flow capacity up to 7,600 CFM.
User Disclaimer: This document is subject to copyright protection and is proprietary to PennBarry. However, PennBarry Corporation authorizes a limited non-exclusive license to use this document or portions of it for the purpose of preparing written product specifications for the above CSI Master Format category. All information in this document as provided by PennBarry is information in nature and is provided without representation or warranty of any kind as to the user or any other party, including, without limitation. Users should consult www.pennbarry.com to verify that this document represents the most current version.
Note to Specifier: This product specification guide is written in accordance to the Construction Specifications Institute (CSI) Master Format - 2016 Edition.
BEGIN SECTION 23 34 23
1. GENERAL
1.1 SUMMARY
A.
Section covers TCI Tubular Centrifugal Inline fan.
1.2 REFERENCE STANDARDS AND CERITIFICATIONS
A. Air Movement and Control Association International (AMCA)
1. 99 – Standards Handbook (2003 Edition)
2. 204 – Standard Balance Quality & Vibration Levels for Fans
3. 210 – Standard Laboratory Methods of Testing Fans for Aerodynamic Performance Rating
4. 211 – Product Rating Program – Product Rating Manual for Fan Air Performance
5. 300 – Reverberant Room Method for Sound Testing of Fans
6. 301- Methods for Calculating Fan Sound Ratings from Laboratory Test Data
7. 311 – Certified Ratings Program Product Rating Manual for Fan Sound Performance
B. Underwriter Laboratories Inc. (UL/cUL)
1. 705 – Standard for Power Ventilators
C. National Fire Protection Agency (NFPA)
1. NFPA 70 – National Electric Code
D. Occupation Safety and Health Administration (OSHA)
1. 1910.212 – General Requirements for Machine Guarding
2. 1910.219 – General Requirements for Guarding Safe use of Mechanical Power Transmission Apparatus
E. National Electric Manufacturer’s Association (NEMA)
1. NEMA MG 1 – Motors and Generators
1.3 SUBMITTALS
A. Submit in accordance with CSI Master Format 01 33 00 Submittal Procedures
B. Exhaust Assembly Performance
1. Provide air performance curves with flow, static pressure, and power
2. Provide sound performance data with sound power levels in eight octave bands and A-weighted overall sound power levels.
3. Provide motor electrical characteristics including current, voltage, phase, cycle, enclosure, nominal speed
4. List all accessories equipped with exhaust assembly.
5. List Standard features of exhaust assembly.
6. Provide Dimensional drawings including weight
7. Provide documentation of AMCA and UL certification
1.4 QUALITY ASSURANCE
A. Exhaust Assembly Performance Certification
1. Exhaust Assembly must be tested in accordance with AMCA Standard 210 and Standard 300.
2. Exhaust Assemblies ratings must conform to AMCA Standards 211 and 311
3. Exhaust Assembly wheels must be dynamically and statically balanced to comply with AMCA 204, fan application category BV-3 (Balance Grade G6.3)
B. Spark Resistance
1. Exhaust Assembly shall be classified for spark resistant construction in accordance with AMCA 99-0401-86
C. Electrical
1. Motors must comply with NEMA standards
1.5 LOGISTICS AND STARTUPS
A. Delivery
1. Units must be examined for damage upon delivery.
2. Visual Damage to packaging or product must be noted upon receipt of delivery, as well as must be noted on the BOL or receipt of delivery.
B. Handling
1. Exhaust Assemblies should be handled in accordance with manufacturer’s instructions and follow all relevant safety precautions in accordance with OSHA regulations.
C. Storage
1. Product must be stored in dry indoor area, protected from potential damage from weather and worksite activities.
2. Long term storage should follow instructions noted in the product’s Installation Operation and Maintenance Manual.
1.6 WARRANTY
A. Manufacturer’s warranty
1. Warranty period is 12 months from date of shipment.
2. See Manufacturer’s warranty for specific terms & conditions.
2. PRODUCTS
2.1. MANUFACTURER
A. Basis of Design: PennBarry, 843 Indianapolis Ave, Lebanon, IN 46032, (765) 483-5800
2.2. LABORATORY EXHAUST SYSTEM – PENNBARRY MODEL TCI
A. Basis of Design: PennBarry Model TCI
B. General Description: Belt drive, roof-mounted commercial laboratory exhaust fan
1. Flow capacity up to 7,600 CFM.
2. Standard atmospheric conditions shall be used to evaluate fan performance (air density 0.075 lb/ft^3) (except as otherwise specified).
3. All fans shall be belt drive, AMCA arrangement 9 according to drawings.
4. Each fan plenum shall be equipped with integral lifting lugs for ease of rigging. Lifting lugs shall be placed to minimize the potential for damage during rigging.
5. All fasteners exposed to corrosive exhaust shall be type 316 stainless, excluding motor and bearing fasteners.
C. Wheel:
1. Fan impeller shall be non-overloading high-efficiency centrifugal wheels, with airfoil style blades designed and tested to maximize performance.
2. Fan impeller shall be constructed of aluminum in accordance with AMCA B spark resistant construction.
3. Fan impeller and housing shall be statically and dynamically tested and balanced in accordance with AMCA 204-05, “Balance Quality and Vibration Levels for Fans”. Fan application category shall be BV-3/6.3 and adhere to all constraints appropriate for this category.
D. Motors and Drive:
1. Fan motors shall be rated as premium efficiency, NEMA frame, 900, 1200, 1800 or 3600 rpm with a TEFC rating and a 1.15 service factor unless used with a VFD, which will result in a 1.0 service factor.
2. When requested, a factory-mounted NEMA 3R disconnect switch shall be mounted to a bolted clip on the fan housing and wired to fan motor by the exhaust assembly manufacturer.
3. All fans shall be belt drive, AMCA arrangement 9 and shall be sized according to the specified drawings.
4. Drive belts and sheaves shall be sized for 150% of the motor horsepower. Drives shall be either adjustable or constant type.
5. Fan motor shall be isolated from outside the exhaust airstream with all motor ventilation originating from ambient, outside air.
6. Motor cover shall be of welded construction.
E. Fan Housing and Construction
1. Fan housing shall be constructed of heavy gauge steel with continuously welded seams. Fan housings with skip-welded seams or other joining methods are unacceptable.
2. Fan inlet shall utilize an aerodynamically designed high-efficiency inlet.
3. Fan housings fabricated of polypropylene, fiberglass, or are bolted together shall not be acceptable.
4. Fan assembly shall be AMCA B spark resistant construction to minimize the sparking potential within the effluent airstream. Other construction types are not acceptable.
5. Fan motor shall be housed outside the exhaust airstream with all motor ventilation originating from ambient, outside air.
6. Provide extended lubrication lines with grease Zerks for easy motor bearing lubrication from fan assembly exterior. Zerks shall be placed on the outside of the fan housing and mounted on welded clips affixed to the fan housing.
7. A bolted oversized access door shall be supplied in the fan housing allowing for impeller inspection and removal of impeller, shaft and bearings without removal of the fan housing.
8. Fan bearings shall be L10-100k concentric lock type.
9. Fan shaft shall be mild steel with an option for 304 or 316 stainless steel.
10. Finish color is gray.
F.  Options/Accessories:

1. Motor Cover:

a) Unit(s) shall be equipped with motor cover providing protective covering.

b) Unit(s) motor cover shall enclose the drive assembly, motor, shaft and bearing.
2. Inlet/Outlet Flanges:

a) Unit(s) shall be provided as an accessory to accommodate flanged duct connections at inlet or discharge, when required.
3. Companion Flanges:

b) Unit(s) shall be provided as an accessory to accommodate slip connections at inlet or discharge, when required.

4. Shaft Seal:

a) Unit(s) shall be equipped with a ceramic material.

5. Safety Service Switch

a) Safety switches shall be provided to allow positive electrical shut-off and safety.

b) Units shall be prewired to a junction box mounted in the motor compartment and equipped with an electrical disconnect device.
c) Unit(s) shall be provided with a NEMA rated enclosures with safety switches available for,

i. NEMA 1 (Indoor) 

ii. NEMA 3R (Indoor or Outdoor Protection)
iii. NEMA 7/9 (EXP Environments – ship loose)
d) Safety switch NEMA 1, and 3R switch shall be factory wired and remaining shall be shipped loose.

e) Safety service switches shall be field wired by a licensed electrician.

6. Outlet guards: 

a) Unit(s) shall be provided with outlet guards.

b) Unit(s) outlet guards shall be heavy gauge coated expanded metal.
7. Drains: 

a) Unit(s) shall be available with provision of drains at the lowest point of the fan tube.

b) Unit(s) drains shall be standard type ¾” NPT internal threads with plug.
8. Paints / Coating:

a) Unit shall be standard Air-Dry Enamel coated, optional Air-Dry Phenolic, or Air Dry Phenolic with UV Protection. 
9. Vibration Isolation:

a) Unit(s) shall be supplied with rubber-in-shear and spring type vibration isolators.

b) Vibration isolators shall be sized to match the weight of each fan.

10. Variable Frequency Drive (VFD): 

a) Unit shall be provided with variable frequency drive (VFD) to meet performance requirement while increasing the efficiency.

b) VFD shall be ideal for both new and retrofit applications.

c) Variable frequency drive shall be available in both loose and factory mounted configuration.
d) VFD shall be compatible to run a Permanent Magnet Motor.

13. Extended Lube Lines: 
13. Unit(s) shall incorporate factory installed extended polyamide lube lines with an option for copper material to be used for the extended lube line
3. EXECUTION
3.1. MANUFACTURER’S INSTRUCTION
A. Follow all manufacturers product usage guidelines and installation instructions
3.2. EXAMINATION
A. Examine fans upon delivery for visual check of components. Verify no visible external damage. Examine area of fan installation for non-satisfactory conditions that may cause
increased maintenance or increased difficulty of installation. Notify Engineer of these conditions and correct as is necessary.
3.3. PREPARATION
A. Verify Roof openings are square and fan dimensions match. Verify fan motor electrical matches building supply power.
3.4. INSTALLATION
A. Follow manufacturer’s recommendations as dictated in the Installation, Operations, & Maintenance Manual
3.5. SYSTEM STARTUP
A. Follow manufacturer’s recommendations as dictated in the Installation, Operations, & Maintenance Manual
3.6. MAINTENANCE
A. Follow manufacturer’s recommended schedule as specified in the Installation, Operations, & Maintenance Manual
B. Failure to comply with proper maintenance will void Manufacturer’s Warranty
END OF SECTION 23 34 23

