PennBarry Fan Guide Specification

Free Standing Centrifugal Fans: Model VCR for belt drive and direct drive
This documents copyrights 2017 PennBarry
Free standing centrifugal fans are high volume capacity fan with backward inclined wheel and airfoil wheel that make them excellent for use in hotels, office buildings, manufacturing plants and hospitals. 

Description

Model VCR is heavy-duty fan compatible to handle a variety of atmospheric conditions including fumes, abrasives, and high temperatures. Customers from industries as diverse as paper, automotive and textiles have found PennBarry backward inclined fans to be suited for their industrial process applications. These fans have high efficiencies and low sound power levels, making them suitable for clean air and lower temperatures only. A wide range of accessories are available to expand the versatility of both fans.

Product Capabilities

· Model: VCR Belt Drive & Direct Drive
• Static pressure up to 18 in. wg.

• Flow capacity up to 460,000 CFM

Note to Specifier: This product specification guide is written in accordance to the Construction Specifications Institute (CSI) Master Format - 2016 Edition.

[REMOVED DESCRIPTION AND MODEL CAPABILITIES TO AVOID REPEATATION OF INFORMATION] 
Note to Specifier: This product specification guide is written in accordance to the Construction Specifications Institute (CSI) Master Format - 2016 Edition.

BEGIN SECTION 23 34 23
1. GENERAL
1.1 SUMMARY
A. Section covers Single and twin unit centrifugal cabinet fan, Zephyr (Z & ZCC), belt drive.
1.2 REFERENCE STANDARDS AND CERITIFICATIONS
A. Air Movement and Control Association Inc. (AMCA):

1. 99 - Standards Handbook

2. 200 - Publication, Air Systems

3. 201-90 - Publication, Fans and Systems

4. 202-88 - Publication, Troubleshooting

5. 203-90 - Publication, Field Performance Measurement of Fan Systems

6. 211-05 - Publication, Certified Ratings Program – Product Rating Manual for Fan Air Performance

7. 300-96 - Standard Reverberant Room Method for Sound Testing of Fans

8. 311-05 - Publication Certified Ratings Program – Product Rating Manual for Fan Sound Performance

9. 99-0401-86 - Classification for Spark Resistant Construction

10. 99-2408-69 - Operating Limits for Centrifugal Fans

B. Air Movement and Control Association Inc. (AMCA), American National Standards Institute (ANSI):

1. 204-05 - Standard Balance Quality and Vibration Levels for Fans

2. 210-99 - Standard Laboratory Methods of Testing Fans for Aerodynamic Performance Rating

C. American National Standards Institute (ANSI):

1. 11-r1999 - Method of Evaluating Load Ratings of Bearings 

D. American Society of Civil Engineers (ASCE):

1. 7-02 - Minimum Design Loads for Building and Other Structures

E. American Society of Heating, Refrigerating and Air Conditioning Engineers, Inc. (ASHRAE):

1. Chapter 45 - 2003 Handbook, HVAC Applications

2. Chapter 7 - 2001 Fundamentals handbook, Sound-Vibration

3. Chapter 32 - 2001 Fundamentals handbook, Duct Design

4. Chapter 18 - 1992 HVAC System and Equipment handbook, Fans

F. American Society for Testing and Materials (ASTM):

1. E330-02 - Standard Test Method for Structural Performance of Exterior Windows, Doors, Skylight and Curtain Walls by Uniform Static Air Pressure Difference

G. National Fire Protection Association (NFPA)

1. 70 - National Electrical Code

2. 90A-02 - Standard for the Installation of Air-Conditioning and Ventilating Systems

3. 92A-06 - Recommend Practice for Smoke-Control System

4. 92B-05 - Standard for Smoke Management System in Malls, Atria, and Large Areas

5. 96-04 - Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations
H. Occupational Safety and Health Administration (OSHA):

1. 1910.212 - General requirements for Machine Guarding

2. 1910.219 - General requirements for guarding safe use of mechanical power transmission apparatus

3. 1926.300 - General requirements for safe operation and maintenance of hand and power tools

I. Underwriters Laboratories (UL):

1. 705 - Standard Power Ventilators

2. Power Ventilators for Smoke Control Systems

3. 762 - Standard Power Roof Ventilators for Restaurant Exhaust Appliances

1.3 SUBMITTALS

A. Submit in accordance with CSI Master Format 01 33 00 Submittal Procedures

B. Fan Performance

1. Provide air performance curves with the flow, static pressure and horsepower

2. Provide sound performance data with sound power levels in eight octave bands, A-weighted overall sound power, and sones level

3. Provide motor electrical characteristics including current, voltage, phase, cycle, enclosure, nominal speed
4. List all accessories equipped with fan

5. List Standard features of fan

6. Provide dimensional drawings including weight

7. Provide documentation of AMCA and UL certification

1.4 QUALITY ASSURANCE

A. Fan Performance Certification

1. Fans rating must conform to tests and procedures performed in accordance with AMCA Publication 211 & 311 and comply with the requirements of the AMCA Certified Ratings Program

2. Fans must bear AMCA licensed Ratings Seal for Air & Sound Performance.

3. Fan shall be UL 705 certified.

B. Electrical

1. Motors must comply with NEMA standards

1.5 LOGISTICS AND STARTUPS
A. Delivery

1. Units must be examined for damage before leaving the factory.
2. Unit shall be inspect for any signs of tampering to carton or unit damage during transit and check for loose, missing or damaged parts. If units are damaged in transit, it is the responsibility of the receiver to make all claims against the carrier.

B. Handling

1. Fans should be handled in accordance with manufacturer’s instructions and follow all relevant safety precautions in accordance with OSHA regulations 
2. Mishandling of units and incorrect lifting causing damage to the fan will void the warranty.

C. Storage

1. Product must be stored on a level, solid surface, preferably indoors. If outside storage is necessary, protect the units against moisture and dirt by encasing the cartons in plastic or in some similar weatherproof material.

2. Long term storage requires special attention and should follow instructions noted in the product’s Operation and Maintenance Manual.

1.6 WARRANTY
A. Manufacturer’s warranty

1. Warranty period is 12 months from date of shipment.

2. See Manufacturer’s warranty for specific terms & conditions.
2. PRODUCTS
1.7  MANUFACTURER
A. PennBarry, Plano, Texas 75074. 

1.8 FREE STANDING CENTRIFUGAL FAN, BELT DRIVE & DIRECT DRIVE.

A. Basis of Design: PennBarry Model: VCR
B. General Description:
1. Unit(s) shall be high volume capacities fan(s) with backward inclined and airfoil type wheels making them suitable for hotels, office buildings, manufacturing plants and hospitals. 

2. Unit(s) shall have below performance capabilities,
· Static pressure up to 18” wg.
· Flow capacity up to 460,000 CFM. 
3. Unit(s) shall be available in sizes ranging from 150 thru 890.

4. Unit(s) shall be belt drive in AMCA arrangement 1, 3, 7, 8, 9 or 10 and direct drive in AMCA arrangement 1, 3, 4, 7, 8. 
5. Unit(s) shall be able to propel air temperatures up to 1000 deg. F in its standard construction.

6. Each fan shall bear the AMCA Licensed Ratings seal for Air and Sound Performance, and shall be UL and cUL listed
7. Unit(s) shall be statically and dynamically balanced.
C. Construction:
1. Unit(s) housing shall be continuously welded and constructed of heavy gauge steel.
2. Unit(s) shall be available in any of these spark resistant construction such as AMCA “A” construction, AMCA “B” construction or AMCA “C” construction (except arrangement 3 and 7).

3. Unit(s) shall be available in below mentioned configuration as per the application / requirement,

a) Heat and smoke configuration

· Unit(s) with heat and smoke configuration shall be listed as per UL 705, UL793, Industrial Risk Insurers (IRI) and Southern Building Code Congress International (SBCCI).

· Unit(s) shall be equipped with steel wheel and extended lube lines.

· Unit(s) shall be compatible with temperature of 500 deg. F for 4 hours and 1000 deg. F. for 1 hour.

D. Fan Housing:
1. Unit(s) housing shall be constructed of heavy gauge steel and shall be continuously welded.

2. Unit(s) housing shall be braced rigidly across the scroll with angle or channel.

3. Unit(s) housing shall be provided with beating supports rigidly and properly braced to provide a firm foundation for shaft and bearings.

E. Wheel:
1. Unit(s) shall consist of very efficient backward inline and airfoil wheel.

2. Unit(s) wheel shall be available in either single width single inlet configuration or double width double inlet configuration.

3. Unit(s) wheel shall be spark resistant and non-overloading.

F. Motors:
1. Motor Type: AC Induction Motor 
a) Motor enclosure shall be available in various options such as ODP, TEFC, SGR and explosion.

b) Motors shall be provided with permanently lubricated, continuous duty ball bearing design furnished at the specified voltage, phase, and enclosure.

c) Labelled with electrical specifications.

d) Drive belts and sheaves shall be sized for 1.5 service factor of the fan operating brake horsepower, and shall be readily and easily accessible for service, if required.

e) Motors shall be capacitor start – capacitor run type, starter not required.

G. Shafts and Bearings : 
1. Unit(s) shall be equipped with heavy duty, self-aligning pillowblock bearing compatible with spilt housing construction.

2. Unit(s) shall utilize durable and long life ball bearing having minimum L10 life rating of 40,000 hours, 80,000 hours and 2, 00,000 hours for Class I and II.
3. Unit(s) shall utilize durable and long life ball bearing having minimum L10 life rating of 80,000 hours and 2, 00,000 hours for Class III and IV.

4. Unit(s) shall consist of precisely turned, ground and polished solid steel shafts.
H. Belt Guard : 
1. Unit(s) shall be equipped totally enclosed belt guards meeting OSHA standards.

I. Options/Accessories:
1. Access Door:
a) Unit(s) shall be provided with bolted or hinged access door.
b) Unit(s) shall be provided with raised access doors in case of high operating temperature conditions.

c) Unit(s) access door hardware shall be stainless steel to resist corrosion.

2. SwingOut Fan:

a) Unit(s) with single width single inlet configurations shall have swingout fan feature for superior accessibility.

b) Unit(s) with swingout feature shall consist of entire rotating assembly and power train mounted on a hinged access door which is reinforced with angle iron framing.
3. Split Housing:

a) Unit(s) greater than size 270 shall be available with split housing construction.

b) Unit(s) with split housing construction shall be able to split vertically or horizontally.

4. Inlet Boxes:

a) Unit(s) shall be equipped with inlet box(s), if required for certain application.

b) Unit(s) with arrangement 3 (SWSI and DWDI) shall be provided with independent bearing pedestal for provision of inlet boxes as it requires bearings to be mounted outside the inlet box.

5. Weather Covers:

a) Unit(s) shall be equipped with weather cover providing protective covering.

b) Unit(s) weather cover can be used for operating temperatures up to 300 deg. F.

c) [Optional] Incase required, unit(s) shall be provided with vented weather covers compatible for operating up to temperatures up to 500 deg. F.

d) Unit(s) weather cover shall enclose the drive assembly, motor, shaft and bearing (only for arrangement 10).
6. Companion Flanges:

a) Unit(s) shall be provided as an accessory to accommodate slip connections at inlet or discharge, when required.

7. Shaft Seal:

a) Unit(s) with single width single inlet configuration shall be equipped with a heat resistant ceramic fiber material.

b) Unit(s) equipped with heat fan packages shall be consist shaft seal as standard accessory.

c) [Optional] Unit(s) shall be supplied with Neoprene, Teflon or stuffing box shaft seals, if required.
8. Variable Inlet Vanes:

a) Unit(s) shall be provided with externally mounted inlet vanes and inlet vanes that are “nested” inside the inlet cone.
b) Variable inlet vanes shall be suitable for manual or motorized operations.
c) Variable inlet vanes shall be compatible for operating temperatures up to 200 deg F.

d) Unit(s) variable inlet vanes shall be constructed with stainless steel rods and bronze iolite bushings.
9. Safety Service Switch

a) Safety switches shall be provided to allow positive electrical shut-off and safety.
b) Units shall be prewired to a junction box mounted in the motor compartment and equipped with an electrical disconnect device (except explosion proof).

c) Unit(s) shall be provided with a wide range of NEMA rated enclosures with safety switches available for,

i. NEMA 1 (Indoor) 

ii. NEMA 3R (Weather proof)

iii. NEMA 4 (outdoor)
iv. NEMA 7

v. NEMA 9

d) Safety switch NEMA 1, 3R and 4X switch shall be factory wired and remaining shall be shipped loose.

e) Safety service switches shall be field wired by a licensed electrician.
10. Inlet and outlet guards : 
a) Unit(s) shall be provided with inlet and outlet guards.

b) Unit(s) inlet guards shall be heavy gauge zinc plated steel wire.

c) Unit(s) outlet guards shall be heavy gauge wire.

11. Drains : 

a) Unit(s) shall be available with provision of drains at the lowest point of scroll.

b) Unit(s) drains shall be standard type ¾” NPT external thread with plug.
12. Paints / Coating:

a) Unit shall be powder coated. Coatings such as standard enamel, airdry phenolic with UV protection or Special coat shall be available.
13. Vibration Isolation:

a) Unit(s) shall be supplied with rubber-in-shear and spring type vibration hangers.

b) Vibration isolators shall be sized to match the weight of each fan

c) In addition to vibration isolation, unit(s) shall be supplied with vibration rails, unitary bases or inertia frames, if required.
d) Vibration isolators shall be sized to match the weight of each fan
14. Variable Frequency Drive (VFD): 

a) Unit shall be provided with variable frequency drive (VFD) to meet performance requirement while increasing the efficiency.

b) VFD shall be ideal for both new and retrofit applications.

c) Variable frequency drive shall be available in both loose and factory mounted configuration. 

15. Discharge Dampers: 
a) Unit(s) shall be provided with gravity shutter(s) or motorized shutter(s) for avoiding backdrafts.

b) Unit(s) shall be provided with discharge manual damper(s) or motorized damper(s) for heavy duty operations.

c) Gravity shutters and dampers shall be able to withstand operating temperatures up to 200 deg F. 

3. EXECUTION
1.9 MANUFACTURER’S INSTRUCTION
A. Follow all manufacturers product usage guidelines and installation instructions

1.10 EXAMINATION
A. Examine fans upon delivery for visual check of components.  Verify no visible external damage.  Examine area of fan installation for non-satisfactory conditions that may cause increased maintenance or increased difficulty of installation. Notify Engineer of these conditions and correct as is necessary. 

1.11 PREPARATION
A. Verify Roof openings are square and fan dimensions match.  Verify fan motor electrical matches building supply power.
1.12 INSTALLATION
A. Follow manufacturer’s recommendations as dictated in the Installation, Operations, & Maintenance Manual

1.13 SYSTEM STARTUP
A. Follow manufacturer’s recommendations as dictated in the Installation, Operations, & Maintenance Manual

1.14 MAINTENANCE 

A. Follow manufacturer’s recommended schedule as specified in the Installation, Operations, & Maintenance Manual

B. Failure to comply with proper maintenance will void Manufacturer’s Warranty

END OF SECTION 23 34 23
