PennBarry Fan Guide Specification

Dynamo (Utility Blower): Model D for belt drive and direct drive 
This documents copyrights 2024 PennBarry
Dynamo fans are used for supply or exhaust applications in commercial, institutional and industrial HVAC systems. At the heart of the Dynamo is a computer-designed, backward inclined, centrifugal wheel. This heavy duty non-overloading wheel assures low noise and high efficiency performance.
[REMOVED DESCRIPTION AND MODEL CAPABILITIES TO AVOID REPEATATION OF INFORMATION] 
Note to Specifier: This product specification guide is written in accordance to the Construction Specifications Institute (CSI) Master Format - 2016 Edition.

BEGIN SECTION 23 34 23
1. GENERAL
1.1 SUMMARY
A. Section covers Utility set centrifugal fan, Dynamo (D), Direct and belt drive.
1.2 REFERENCE STANDARDS AND CERITIFICATIONS
A. Air Movement and Control Association Inc. (AMCA):

1. 99 - Standards Handbook

2. 200 - Publication, Air Systems

3. 201-90 - Publication, Fans and Systems

4. 202-88 - Publication, Troubleshooting

5. 203-90 - Publication, Field Performance Measurement of Fan Systems

6. 211-05 - Publication, Certified Ratings Program – Product Rating Manual for Fan Air Performance

7. 300-96 - Standard Reverberant Room Method for Sound Testing of Fans

8. 311-05 - Publication Certified Ratings Program – Product Rating Manual for Fan Sound Performance

9. 99-0401-86 - Classification for Spark Resistant Construction

10. 99-2408-69 - Operating Limits for Centrifugal Fans

B. Air Movement and Control Association Inc. (AMCA), American National Standards Institute (ANSI):

1. 204-05 - Standard Balance Quality and Vibration Levels for Fans

2. 210-99 - Standard Laboratory Methods of Testing Fans for Aerodynamic Performance Rating

C. American National Standards Institute (ANSI):

1. 11-r1999 - Method of Evaluating Load Ratings of Bearings 

D. American Society of Civil Engineers (ASCE):

1. 7-02 - Minimum Design Loads for Building and Other Structures

E. American Society of Heating, Refrigerating and Air Conditioning Engineers, Inc. (ASHRAE):

1. Chapter 45 - 2003 Handbook, HVAC Applications

2. Chapter 7 - 2001 Fundamentals handbook, Sound-Vibration

3. Chapter 32 - 2001 Fundamentals handbook, Duct Design

4. Chapter 18 - 1992 HVAC System and Equipment handbook, Fans

F. American Society for Testing and Materials (ASTM):

1. E330-02 - Standard Test Method for Structural Performance of Exterior Windows, Doors, Skylight and Curtain Walls by Uniform Static Air Pressure Difference

G. National Fire Protection Association (NFPA)

1. 70 - National Electrical Code

2. 90A-02 - Standard for the Installation of Air-Conditioning and Ventilating Systems

3. 92A-06 - Recommend Practice for Smoke-Control System

4. 92B-05 - Standard for Smoke Management System in Malls, Atria, and Large Areas

5. 96-04 - Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations
H. Occupational Safety and Health Administration (OSHA):

1. 1910.212 - General requirements for Machine Guarding

2. 1910.219 - General requirements for guarding safe use of mechanical power transmission apparatus

3. 1926.300 - General requirements for safe operation and maintenance of hand and power tools

I. Underwriters Laboratories (UL):

1. 705 - Standard Power Ventilators

2. Power Ventilators for Smoke Control Systems

3. 762 - Standard Power Roof Ventilators for Restaurant Exhaust Appliances

1.3 SUBMITTALS

A. Submit in accordance with CSI Master Format 01 33 00 Submittal Procedures

B. Fan Performance

1. Provide air performance curves with the flow, static pressure and power

2. Provide sound performance data with sound power levels in eight octave bands, A-weighted overall sound power, and sones level

3. Provide motor electrical characteristics including current, voltage, phase, cycle, enclosure, nominal speed
4. List all accessories equipped with fan

5. List Standard features of fan

6. Provide dimensional drawings including weight

7. Provide documentation of AMCA and UL certification

1.4 QUALITY ASSURANCE

A. Fan Performance Certification

1. Fans rating must conform to tests and procedures performed in accordance with AMCA Publication 211 & 311 and comply with the requirements of the AMCA Certified Ratings Program

2. Fans must bear AMCA licensed Ratings Seal for Air & Sound Performance.

B. Electrical

1. Motors must comply with NEMA standards

1.5 LOGISTICS AND STARTUPS
A. Delivery

1. Units must be examined for damage before leaving the factory.
2. Unit shall be inspected for any signs of tampering to carton or unit damage during transit and check for loose, missing or damaged parts. If units are damaged in transit, it is the responsibility of the receiver to make all claims against the carrier.

B. Handling

1. Fans should be handled in accordance with manufacturer’s instructions and follow all relevant safety precautions in accordance with OSHA regulations 
2. Mishandling of units and incorrect lifting causing damage to the fan will void the warranty.

C. Storage

1. Product must be stored on a level, solid surface, preferably indoors. If outside storage is necessary, protect the units against moisture and dirt by encasing the cartons in plastic or in some similar weatherproof material.

2. Long term storage requires special attention and should follow instructions noted in the product’s Operation and Maintenance Manual.

1.6 WARRANTY
A. Manufacturer’s warranty

1. Warranty period is 12 months from date of shipment.

2. See Manufacturer’s warranty for specific terms & conditions.
2. PRODUCTS
1.7  MANUFACTURER
A. PennBarry, Lebanon, IN 46052. 

1.8 FREE STANDING CENTRIFUGAL FAN, DIRECT or BELT DRIVE
A. Basis of Design: PennBarry Model Dynamo (D)
B. General Description: 

1. Unit(s) shall be suitable for exhaust and supply in heavy-duty applications.
2. Unit(s) construction features shall consist of be single width single inlet fan type, Class I, Arrangement 4 (Direct Drive) / Arrangement 10 (Belt Drive) for general purpose air moving devices.
3. Unit(s) shall be field rotatable in both clockwise or anti clockwise to any of eight discharge positions.

4. Unit(s) shall have below performance capabilities,
a) Model: D, Direct Drive Units 

· Static pressure up to 3.0” wg. 

· Flow capacity up to 5,000 CFM. 

· Available in sizes 6” to 24”. 

b) Model: D (B), Belt Drive Units 

· Static pressure up to 5.0” wg. 

· Flow capacity up to 45,000 CFM. 

· Available in sizes 6” to 44”.

5. Each fan shall bear the AMCA Licensed Ratings seal for Air and Sound Performance, and shall be UL and cUL listed
6. Unit(s) shall be statically and dynamically balanced.
C. Construction [Optional] :

1. Unit(s) shall be available in following configuration as per the application / requirement,

a) Curb mounted utility set with integral inlet box.

· Unit(s) shall include integral galvanized curb cap and fully welded inlet box.

· Units) shall consist of vented weather cover.

· Unit(s) shall be provided with high temperature sealant between scroll casing and sides

· Unit(s) shall be designed for high velocity discharge.

b) Grease Exhaust configuration

· Unit(s) with Grease Exhaust / Fatrap configuration shall be UL 762 listed 

· Unit(s) shall meet the requirements according to NFPA 96.
· Unit(s) shall include pre-wired weather resistant junction box and grease collector box.

· [Optional] Unit(s) consisting of upblast mounting shall be attached to fully welded inlet plenum and mounted on a curb cap

· Unit(s) shall consist of integral galvanized curb caps.
· Unit(s) shall be provided with high temperature sealant between scroll casing and sides

· Unit(s) shall be designed for high velocity discharge.

c) Heat and smoke configuration

· Unit(s) with heat and smoke configuration shall be listed as per UL 705, UL793, Industrial Risk Insurers (IRI) and Southern Building Code Congress International (SBCCI).

· Unit(s) shall be equipped with steel wheel and extended lube lines.

· Unit(s) shall be compatible with temperature of 500 deg. F for 4 hours and 1000 deg. F. for 41 minutes.
d) High wind hurricane zone configuration

· Unit(s) with high wind configuration shall withstand 150 MPH winds in accordance with Miami-Dade and Florida Building Code Standards.

D. Wheel:
1. Unit(s) shall consist of backward inclined centrifugal wheels.

2. Wheel shall be constructed of durable aluminum (optional steel for heat and smoke removal configuration).

3. Unit(s) wheel shall be spark resistant and non-overloading.

4. Unit(s) wheel assembly shall be fully welded for maximum performance and reliability.

5. Unit(s) wheel shall be statically and dynamically balanced.

E. Motors:
1. Motor Type: AC Induction Motor [ Belt Drive]

a) Motor enclosure shall be available in various options such as ODP, TEFC, EXP.

b) Motors shall be provided with permanently lubricated, continuous duty ball bearing design furnished at the specified voltage, phase, and enclosure.

c) Labelled with electrical specifications.

d) Drive belts and sheaves shall be sized for 1.5 service factor of the fan operating brake horsepower, and shall be readily and easily accessible for service, if required.

e) Single Phase Induction Motors shall be capacitor start – capacitor run type, starter not required.

2. Motor Type: Electronically Commutated Motor [Direct Drive]

a) Motor shall be suitable for continuous duty operation

b) Motor enclosure shall be available in wide range option such as open drip proof (ODP), open air over (OPAO) & totally enclosed fan cooled (TEFC) motors.

c) Unit(s) motor(s) shall be permanently lubricated, heavy duty ball bearing type to match with the fan load and pre-wired to the specific voltage and phase

F. Shafts and Bearings:

1. Unit(s) shall consist of precisely turned, ground and polished solid steel shafts.

2. Unit(s) shafts shall be designed to withstand minimum of 125% of maximum catalogued operating speed.

3. Heavy duty ball bearings shall be rated for a minimum L50 life exceeding 200,000 hours.

4. In special scenario, if desired for another material of unit’s hardware, stainless steel shafts shall be provided.

G. Housing / Hood:

1. Unit(s) housing shall be heavy gauge zinc coated galvanized steel.

2. Unit(s) housing shall be corrosion resistant.

3. Housing shall be field rotatable to any of eight incremental discharge position
H. Housing Supports and Drive Frame:
1. The entire operating assembly shall be mounted on heavy duty support frame.
I. Access Door:

1. Unit(s) scroll shall be equipped with a bolted, gasket access door for cleaning and inspection
2. [Optional] Unit(s) shall be provided with quick release type door for periodic cleaning, in addition to standard gasket access door.

J. Options/Accessories:
1. Damper:
a) Unit(s) shall be provided with gravity back draft damper or control damper with actuator (120V, 230V, and 460V v transformer) at outlet. (Except for unit(s) with top-angular-down, bottom-angular-down discharge position.)
b) Damper(s) shall remain balanced for air velocity below 4000 FPM.

2. Service Switches:
a) Safety switches shall be provided to allow positive electrical shut-off and safety. 

b) Units shall be prewired to a junction box mounted in the motor compartment and equipped with an electrical disconnect device (except explosion proof).

c) Unit(s) shall be provided with a wide range of NEMA rated enclosures with safety switches available for,

i. NEMA 1 (Indoor) 

ii. NEMA 3R (Weather Resistant)

iii. NEMA 4 (outdoor) 

iv. NEMA 7 (explosion) 

d) Disconnects shall be field wired by a licensed electrician.
3. Inlet and outlet guards: 
a) Unit(s) shall be provided with inlet and outlet guard.

b) Guards shall be constructed of expanded steel in a removable frame attached to the fan housing.
4. Drain connections: 

a) Unit(s) shall be provided with mechanically fastened and sealed drain connection at the lowest point of scroll.

5. Paints / Coating:

a) Unit shall be wet or powder coated. Coatings such as Polyester, Epoxy / Epoxy with UV, Phenolic Epoxy / Phenolic Epoxy with UV or Special Coat shall be available.

6. Ventilated weather cover: 

a) Unit(s) shall be provided galvanized steel cover called as weather cover.

b) Unit(s) weather cover shall protect the shafts, bearings, motor and drive components.
7. Extended lube lines: 

a) Unit(s) shall be provided with extended lube lines, in case weather cover is installed or when access to the bearing is unavailable.

b) Extended lube lines shall be preloaded at the factory.

8. Vibration Isolation:

a) Unit(s) shall be provided with multidirectional rubber-in-shear and spring type isolators.

b) There shall be no metal-to-metal contact between drive assembly and fan structure

c) Vibration isolators shall be sized to match the weight of each fan
9. Firestat Switch: 

a) Unit(s) shall be include a safety device mounted below the fan.

b) Unit(s) shall be provided with firestat switch to disconnect fan, when the temperature of the air being exhausted exceeds preset rating.

10. Variable Frequency Drive (VFD): 
a) Unit shall be provided with variable frequency drive (VFD) to meet performance requirement while increasing the efficiency.

b) VFD shall be ideal for both new and retrofit applications.

c) Variable frequency drive shall be available in both loose and factory mounted configuration. 

3. EXECUTION
1.9 MANUFACTURER’S INSTRUCTION
A. Follow all manufacturers product usage guidelines and installation instructions

1.10 EXAMINATION
A. Examine fans upon delivery for visual check of components.  Verify no visible external damage.  Examine area of fan installation for non-satisfactory conditions that may cause increased maintenance or increased difficulty of installation. Notify Engineer of these conditions and correct as is necessary. 

1.11 PREPARATION
A. Verify Roof openings are square and fan dimensions match.  Verify fan motor electrical matches building supply power.
1.12 INSTALLATION
A. Follow manufacturer’s recommendations as dictated in the Installation, Operations, & Maintenance Manual

1.13 SYSTEM STARTUP
A. Follow manufacturer’s recommendations as dictated in the Installation, Operations, & Maintenance Manual

1.14 MAINTENANCE 

A. Follow manufacturer’s recommended schedule as specified in the Installation, Operations, & Maintenance Manual

B. Failure to comply with proper maintenance will void Manufacturer’s Warranty

END OF SECTION 23 34 23
