PennBarry Fan Guide Specification 
Tubular Inline Fan: Model TUB™ 
This document copyrights© 2025 PennBarry
TUB is a tubular inline centrifugal fan that is designed for versatility in low to high pressure inline applications used in commercial, institutional, or industrial applications. TUB is suitable for warehouse ventilation, space pressurization, and general supply / exhaust ventilation. 
The TUB features a durable welded CNC precision rolled concentric housing with a highly efficient centrifugal wheel. Engineered to provide maximum performance, efficiency, and reliability.
Product Capabilities
-     Belt Drive
-
 Airfoil and Backward Incline
-     Fan Airflow capacity up to 221,450 CFM.
-     Static pressure up to 10.0 in. wg.

-     Horizontal, Vertical, and Rooftop arrangements.
User Disclaimer: This document is subject to copyright protection and is proprietary to PennBarry. However, PennBarry Corporation authorizes a limited non-exclusive license to use this document or portions of it for the purpose of preparing written product specifications for the above CSI MasterFormat category. All information in this document as provided by PennBarry is information in nature and is provided without representation or warranty of any kind as to the user or any other party, including, without limitation. Users should consult  www.pennbarry.com to verify that this document represents the most current version.
Note to Specifier: This product specification guide is written in accordance to the Construction
Specifications Institute (CSI) Master Format - 2016 Edition.
BEGIN SECTION 23 34 23
1.   GENERAL
1.1 SUMMARY
A.         Section covers Tubular Centrifugal Fan, Inline and Rooftop.
1.2 REFERENCE STANDARDS AND CERITIFICATIONS
A.         Air Movement and Control Association International (AMCA)
1.         99 – Standards Handbook (2003 Edition)
2.         204 – Standard Balance Quality & Vibration Levels for Fans
3.         210 – Standard Laboratory Methods of Testing Fans for Aerodynamic
Performance Rating
4.         211 – Product Rating Program – Product Rating Manual for Fan Air
Performance
5.         300 – Reverberant Room Method for Sound Testing of Fans
6.         301- Methods for Calculating Fan Sound Ratings from Laboratory T
Data
7.         311 – Certified Ratings Program Product Rating Manual for Fan Sound
Performance

B.         American National Standards Institute (ANSI/AIHA)
1.         Z9.5-2003 Laboratory Ventilation
C.         American Society of Heating, Refrigeration and Air Conditioning Engineering
(ASHRAE)
1.         Laboratory Design Guide (2002 Edition) 
D.         Underwriter Laboratories Inc. (UL/cUL)
1.         705 – Standard for Power Ventilators
E.         National Fire Protection Agency (NFPA)
1.         NFPA 70 – National Electric Code
F.         Occupation Safety and Health Administration (OSHA)
1.         1910.212 – General Requirements for Machine Guarding
2.         1910.219 – General Requirements for Guarding Safe use of Mechanical
Power Transmission Apparatus
G.         National Electric Manufacturer’s Association (NEMA)
1.         NEMA MG 1 – Motors and Generators
1.3 SUBMITTALS
A.         Submit in accordance with CSI Master Format 01 33 00 Submittal Procedures
B.         Fan Performance
1.         Provide air performance curves with flow, static pressure, and power
2.
Provide sound performance data with sound power levels in eight octave bands and A-weighted overall sound power levels.
3.
Provide motor electrical characteristics including current, voltage, phase, cycle, enclosure, nominal speed.
4.         List all accessories equipped with exhaust assembly.
5.         List Standard features of exhaust assembly.
6.         Provide Dimensional drawings including weight
7.         Provide documentation of AMCA certification
1.4 QUALITY ASSURANCE
A.         Fan Performance Certification
1.         Fans performance ratings must conform to tests and procedures 

             performed in accordance with AMCA Publication 211 & 311.
2.          Fans must bear AMCA licensed Ratings Seal for Air & Sound 

             Performance.
B.         Electrical
1.         Motors must comply with NEMA standards
1.5 LOGISTICS AND STARTUPS 

A.
Delivery
1.         Units must be examined for damage upon delivery.
2.
Visual Damage to packaging or product must be noted upon receipt of delivery, as well as must be noted on the BOL or receipt of delivery.
B.         Handling
1.
Fans should be handled in accordance with manufacturer’s instructions and follow all relevant safety precautions in accordance with OSHA regulations.
C.         Storage
1.
Product must be stored in dry indoor area, protected from potential damage from weather and worksite activities.
2.         Long term storage should follow instructions noted in the product’s
Installation Operation and Maintenance Manual.
1.6 WARRANTY
A.         Manufacturer’s warranty
1.         Warranty period is 12 months from date of shipment.
2.         See Manufacturer’s warranty for specific terms & conditions.
2.   PRODUCTS
2.1. MANUFACTURER
A.     PennBarry, Lebanon, Indiana 46052.
2.2. TUBUBLAR CENTRIFUGAL INLINE OR ROOF MOUNTED FAN, BELT DRIVE


A.
Basis of Design: PennBarry Model AWX


B.     General Description: 

1.      Unit(s) shall have inline flow tube configuration, suitable for supply, exhaust or return air applications. 



2.       Belt drive, Inline and roof-mounted commercial 
a.   Flow capacity up to 221,450 CFM.
b.   Standard atmospheric conditions shall be used to evaluate fan 

  performance (air density 0.075 lb/ft^3) (except as otherwise specified).


3.        All fans shall be belt drive, AMCA arrangement 1, 3, or 9 according to drawings. 


4.        Unit(s), in its standard construction, shall be able to propel air temperatures up



         to 180 deg. F for arrangement 3 and 200 deg. F arrangement 1 and 9.

5.       Final complete fan assembly shall be vibration tested and mechanically balanced              as per AMCA 204 Grade BV3 / ANSI S2.19 G 6.3, 0.15 in/sec and the results recorded on a label placed on the fan assembly.
C.     Wheel:
1.   Unit(s) shall consist of very efficient [Backward, Airfoil] inline 

2.   Unit(s) wheel shall be [lightweight aluminum material, spark resistant and non-overloading; steel material, coated and non-overloading].
3.   Hub secured by set screws to fan shaft.
4.   Assembly shall be statically and dynamically balanced.
5.  Units(s) wheel shall be [lightweight aluminum material, spark resistant and non-  overloading; steel material, coated and non-overloading].
D.     Motors:
1. Motor Type: 

a. AC Induction Type

i. Motor enclosure shall be available in various options such as ODP, TEFC, and TEXP.
ii. Motors shall be provided with regreasable or permanently lubricated, continuous duty ball bearing design furnished at the specified voltage, phase, and enclosure.

iii. Motor labeled with electrical specifications.

iv. NEMA Frame

v. Motor speeds [750,900,1000,1200,1500,1800,3000,3600]
vi. Service factor of 1.15 unless used with a VFD which will result in a 1.0 service factor
vii. Belts and sheaves shall be sized for 1.5 service factor of the fan operating brake horsepower, and shall be readily and easily accessible for service, if required.
b. Permanent Magnet Type
i. Motor enclosure: [TEFC, TENV]
E.     Housing:
1.   Fan housing drum shall be constructed of heavy gauge [Aluminum, Stainless Steel, Mild Steel]. with continuously welded seams. Fan housings with skip-welded seams or other joining methods are unacceptable.
2.
Fan housing constructed of mild steel fan material shall be coated with enamel as standard or optional other available coating as made available by coating suppliers and as indicated on the fan schedule.
3.   Fan assembly shall be available in either AMCA B or C spark resistant construction to minimize the sparking potential within the effluent airstream. 
4.   Provide extended lubrication lines with grease Zerks for easy fan bearing lubrication from fan assembly exterior. Zerks shall be placed on the outside of the fan housing and mounted to the fan housing.
5.   Straightening vanes shall be standard construction to assure maximum efficiency and lowest noise levels. Constructed of heavy gauge steel.
F.     Housing Supports:

1. Units shall include supports to be constructed of steel which is welded to the housing drum that is suitable to handle the weights of the motor and impeller.
G.     Shafts and Bearings:

1. Unit(s) shall utilize durable and long-life ball bearing having minimum L10 life rating of [40,000, 80,000, 120,000, 200,000] hours.

2. Unit(s) shall consist of precisely turned, ground and polished solid steel shafts.

H.     Options/Accessories

1. Coatings 

a) Air Dry Coatings: [Enamel, Epoxy, Epoxy (w/UV), Phenolic, Phenolic (w/UV), Phenolic Epoxy, Phenolic Epoxy (w/UV)]
1. Galvanized, stainless, and aluminum parts to be uncoated unless specified otherwise.

b) Or optional other available coating as made available by coating suppliers and as indicated on the fan schedule.
2. Windband and Damper: prevents reverse flow of air from entering building when fan is off.

a) Gravity operated.
b) The frame material shall match Fan Housing.
c) Windband shall be [Aluminum, Stainless Steel, Galvanized Steel].
d) Butterfly type [with, without] Magnetic Damper Latches.
e) Blade shall be [Aluminum, Stainless Steel, Galvanized Steel].
3. Curb Cap: for rooftop upblast configurations.
a) Material: Heavy gauge welded gussets and lifting supports. Material to match Fan Housing.
4. Speed Controller 

a) Shipped loose.
5. Service Switch
a) NEMA 3R switches shall be mounted to a bolted on the fan housing and wired to fan motor.

b) NEMA 7 or 9 shall be shipped loose and not wired.
6. Roof Curb

a) Type: Flat, self-flashing curb

b) Material: 14 ga [Aluminum, Galvanized Steel]
c) Insulation Thickness shall be 1.5 inches all around (if required)
d) Liner: Welded steel sheet to hold insulation in place (if required)
e) Height: [12, 14, 16, 18, 24]
7. Vibration Isolation
a) Unit(s) shall be supplied with [Rubber-in-shear, Spring] isolators. 

b) Vibration isolators shall be sized to match the weight of each fan.

c) [Direct, Rail] mount to fan housing.

d) Mounted by others and excluded for Rooftop Upblast arrangements.

e) Rail mounts shall be constructed of heavy gauge steel.
8. Access door
a) Unit(s) shall be provided with [bolted; hinged] access door.
b) Material to match Fan Housing.

9. Drains
a) Unit(s) shall be available with provision of drains at the lowest point of drum.
b) Unit(s) drains shall be standard type ¾” NPT internal threads with plug.
10. Weather Cover or Belt guard
a) Units(s) shall be equipped with belt cover providing protective covering. When weather cover is furnished, belt guard will not be provided.
11. Companion Flanges:
a) Units(s) shall be provided as an accessory to accommodate slip connections at inlet or discharge, when required.
3.   EXECUTION
3.1. MANUFACTURER’S INSTRUCTION
A.     Follow all manufacturers product usage guidelines and installation instructions
3.2. EXAMINATION
A.
Examine fans upon delivery for visual check of components. Verify no visible external damage. Examine area of fan installation for non-satisfactory conditions that may cause increased maintenance or increased difficulty of installation. Notify Engineer of these conditions and correct as is necessary.
3.3. PREPARATION
A.
Verify Roof openings are square and fan dimensions match. Verify fan motor electrical matches building supply power.
3.4. INSTALLATION
A.
Follow manufacturer’s recommendations as dictated in the Installation, Operations, & Maintenance Manual
3.5. SYSTEM STARTUP
A.
Follow manufacturer’s recommendations as dictated in the Installation, Operations, & Maintenance Manual
3.6. MAINTENANCE
A.     Follow manufacturer’s recommended schedule as specified in the Installation, Operations,
& Maintenance Manual
B.     Failure to comply with proper maintenance will void Manufacturer’s Warranty
END OF SECTION 23 34 23
